## Substation Earthing
TOUCH AND STEP VOLTAGE CALCULATION
| Input Variables |  |  |  |  | Symbol | Value
| Maximum Grid Curent |  |  |  |  | IG | 800 | A | [13 empty] | Lyy
| Earth Fault Duration (Max. Clearing Time) |  |  |  |  | ts | 1 | s | [13 empty] | 2.3333 | m
| Soil Resistivity |  |  |  |  | r | 100 | Ω-m
| Resisivity of surface material |  |  |  |  | ps | 2500 | Ω-m
| Number of earth rods on grid periphery |  |  |  |  | nr | 6
| Diameter of grid conductors |  |  |  |  | d | 0.0123 | m | [16 empty] | Ly
| Diameter of earth stake |  |  |  |  | Nd | 0.019 | m | [15 empty] | 7 |  | m
| Grid length in (x direction) |  |  |  |  | Lx | 14
| Grid length (y direction) |  |  |  |  | Ly | 7
| Number of Conductors in 'x' direction |  |  |  |  | nx | 4
| Number of Conductors in 'y' direction |  |  |  |  | ny | 3
| Depth of buried ground grid conductor |  |  |  |  | h | 0.5
| Depth of substation surface material |  |  |  |  | hs | 0.1
| Length of each rod in the ground |  |  |  |  | Lr | 6
| Output Variables |  |  |  |  | Symbol | Value
| Length of one grid in the 'x' direction |  |  |  |  | Lxx | 3.5 | [8 empty] | Lxx | 3.5 |  | m
| Length of one grid in the 'y' direction |  |  |  |  | Lyy | 2.3333
| Spacing between parallel conductors |  |  |  |  | D | 2.3333 | [5 empty] | Lx | 14 | m
| Total length of grid conductor in the grid |  |  |  |  | LC | 77
| Peripheral length of the grid |  |  |  |  | Lp | 42 | [14 empty] | Earth Stake(s)
| Total length of all ground rods |  |  |  |  | LR | 36 |  | Substation Surface
| Total area of earth grid |  |  |  |  | A | 98 | [8 empty] | hs
| Surface Layer Derating Factor |  |  |  |  | CS | 0.70207 |  |  |  | Surface Material |  |  |  |  | 0.1 |  | m |  | h
| Coefficient 1 for L:W Ratio |  |  |  |  | k1 | 1.33 | [12 empty] | 0.5 | m
Lr
[24 empty] | 6 |  | m
Buried Earth Grid Conductor
| Coefficient 2 for L:W Ratio |  |  |  |  | k2 | 5.8
Total Grid Resistance
(1) |  | Resistance of Grid Conductors Alone, R1, |  |  |  |  | (IEEE 80 - Eq. 54)
[9 empty] | = | 5.0134 |  | Ω
(2) |  | Resistance of Earth Rods Alone, R2: |  |  |  | (IEEE 80 - Eq. 55)
[9 empty] | = | 12.0065 |  | Ω
(3) |  | Mutual Resistance between Grid Conductors and Earth Rods, Rm: | [6 empty] | (IEEE 80 - Eq. 56)
[9 empty] | = | 3.6338 |  | Ω
(4) |  | Effective Resistance to Remote of Earth, RG: |  |  |  |  | (IEEE 80 - Eq. 53)
[9 empty] | = | 4.8182 |  | Ω
Allowable Touch and Step Voltages
(5) |  | Allowable Touch Voltage, Etouch70: |  | (IEEE 80 - Eq. 33)
[9 empty] | = | 571 |  | Volts
(6) |  | Allowable Step Voltage, Estep70: |  | (IEEE 80 - Eq. 30)
[9 empty] | = | 1811 |  | Volts
Actual Touch and Step Voltages
(7) |  | Grid depth corrective weighting factor, Kh: |  |  |  |  | (IEEE 80 - Eq. 83)
[9 empty] | = | 1.2247
(8) |  | Effective number of parallel conductors, n: |  |  |  |  | (IEEE 80 - Eq.s 84, 85 and 86)
[9 empty] | = | 3.7762
(9) |  | Grid geometrical factor, Km: |  |  |  |  | (IEEE 80 - Eq. 81)
[9 empty] | = | 0.59952
(10) |  | Irregularity factor, Ki: |  |  |  |  | (IEEE 80 - Eq. 89)
[9 empty] | = | 1.2029
(11) |  | Effective Buried Length (Touch Voltage), LM: |  |  |  |  | (IEEE 80 - Eq. 91)
[9 empty] | = | 195.4463 |  | m
(12) |  | Effective Buried Length (Step Voltage), LS: |  |  |  |  | (IEEE 80 - Eq. 93)
[9 empty] | = | 63.078 |  | m
(13) |  | Step Voltage Spacing Factor, KS: |  |  | (IEEE 80 - Eq. 94)
[9 empty] | = | 0.18122
(14) |  | Mesh Voltage, Em: | (IEEE 80 - Eq. 80)
[9 empty] | = | 296 |  | Volts |  |  | Touch Voltage within limit (571 Volts)
(15) |  | Step Voltage, Es: | (IEEE 80 - Eq. 92)
[9 empty] | = | 276.4709 |  | Volts |  |  | Step voltage within limit (1811 Volts)
Notes
1) | Refer to Page 2 of this calculation for all formulas used.

## FORMULAS
SUBSTATION TOUCH AND STEP VOLTAGES CALCULATION - EQUATIONS FROM IEEE 80
| (1) | [6 empty] | (10)
(11)
(2)
(12)
(3)
(13)
(4)
(14)
(5)
(15)
(6)
(16)
(7)
(17)
(8)
| (9) | [6 empty] | (18)
DHTU-2 PROJECT SUBSTATION TOUCH AND STEP VOLTAGE CALCULATION
[7 empty] | Document No. |  | Sheet | Revision
A |  |  | Issued for Review | SMC | TJH | RV | CA-25554-EL-00-006 |  | 2 of 2 | 0
Rev. |  | Date | Description | Prep. | Chkd | Appr.

## Notes (hidden)
1
2 | 1 | Objective
3 |  | To verify the step and touch potentials are within tolerable limits
4
5 | 2 | Assumptions
6 |  | Soil resistivity is 100 Ohm.m
7
8 | 3 | Method
9
10 |  | Check Step and Touch Potential using IEEE80
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51