## 400V AC Motors
CABLE SIZING CHART FOR 400V MOTOR FEEDER
CONDUCTOR OPERATING TEMPERATURE |  |  |  |  | 90 | °C |  |  | CABLE DERATING FACTORS |  |  |  |  | General Notes:
AMBIENT AIR TEMPERATURE |  |  |  |  | 40 | °C |  |  | Temperature Derating Factor |  |  | 1.05 |  | 1 | AMPACITY OF CABLES SHOWN IN THE TABLE ARE BASED ON AMB. TEMP 45 DEG C
SUPPLY VOLTAGE |  |  |  |  | 400 | V |  |  | Grouping Factor |  |  | 0.85 |  | 2 | CABLE DATA IS TAKEN FROM DRAKA CABLE CATALOGUE (FLEXFLAME RFOU 0.6/1kV P1/P8 Power Cable)
FREQUENCY / NO. OF PHASES |  |  |  |  | 50Hz / 3f | [8 empty] | 3 | MOTOR DATA IS TAKEN FROM BROOK CROMPTON DATA (4 POLE HIGH EFF. EExd MOTORS)
ALLOWABLE CABLE VOLTAGE DROP | [8 empty] | TOTAL DERATING FACTOR |  |  | 0.8925 |  |  | - http://www.brookcrompton.com/pdf-files/2205E_EEx_d_issue%202e.pdf
| STARTING CONDITION |  |  |  | 15%
| RUNNING CONDITION |  |  |  | 5%
POWER FACTOR
| STARTING CONDITION |  |  |  | 0.3
MAXIMUM CABLE LENGTH |  |  |  |  | 3000 | M
| CSA. mmSQ | [5 empty] | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 2x95 | 2X120 | 2X150 | 2X185 | 2X240 | 3x95 | 3x120
| Volt Drop (mV/A/m) R | [5 empty] | 7.6386 | 4.7786 | 3.1886 | 1.9186 | 1.2386 | 0.8126 | 0.6076 | 0.4696 | 0.3486 | 0.2736 | 0.2326 | 0.2046 | 0.1786 | 0.1548 | 0.1368 | 0.1163 | 0.1023 | 0.0893 | 0.0774 | 0.0912 | 0.077533
| Volt Drop (mV/A/m) X | [5 empty] | 0.103 | 0.096 | 0.09 | 0.084 | 0.08 | 0.079 | 0.076 | 0.076 | 0.074 | 0.073 | 0.072 | 0.072 | 0.072 | 0.072 | 0.0365 | 0.036 | 0.036 | 0.036 | 0.036 | 0.024333 | 0.024
| AMPACITY (A) | [5 empty] | 21 | 28 | 36 | 50 | 67 | 89 | 110 | 137 | 169 | 205 | 237 | 272 | 311 | 365 | 410 | 474 | 544 | 622 | 730 | 615 | 711
| DERATED AMPACITY (A) | [5 empty] | 18.7425 | 24.99 | 32.13 | 44.625 | 59.7975 | 79.4325 | 98.175 | 122.2725 | 150.8325 | 182.9625 | 211.5225 | 242.76 | 277.5675 | 325.7625 | 365.925 | 423.045 | 485.52 | 555.135 | 651.525 | 548.8875 | 634.5675
MOTOR | EFF | PF | FLA | FLA/LRC | LRC |  | MAXIMUM LENGTH (M)
(KW) |  |  | (AMPS) |  | (AMPS)
0.55 | 0.75 | 0.67 | 1.5799 | 5.3 | 8.3733 |  | 2432.2749
0.75 | 0.75 | 0.75 | 1.9246 | 5.3 | 10.2002 |  | 1789.042 | 2843.4171
1.1 | 0.77 | 0.73 | 2.8247 | 5 | 14.1235 |  | 1251.4237 | 1988.2603 | 2957.5967
1.5 | 0.79 | 0.76 | 3.6061 | 5.5 | 19.8338 |  | 942.5648 | 1498.3243 | 2230.2111
2.2 | 0.81 | 0.78 | 5.0261 | 5.8 | 29.1517 |  | 659.3925 | 1048.5428 | 1561.3702 | 2563.6182
3 | 0.83 | 0.75 | 6.9562 | 6.5 | 45.2155 |  | 494.9683 | 786.6787 | 1170.7033 | 1919.9392 | 2922.3668
4 | 0.845 | 0.81 | 8.4355 | 6 | 50.6129 |  | 378.7322 | 602.5503 | 897.8003 | 1475.8027 | 2253.13
5.5 | 0.86 | 0.83 | 11.1219 | 6.8 | 75.6288 |  | 280.5258 | 446.457 | 665.4934 | 1094.779 | 1673.0948 | 2484.2287 | 2484.2287
7.5 | 0.87 | 0.84 | 14.8134 | 7 | 103.6938 |  | 208.1835 | 331.38 | 494.06 | 813.0747 | 1243.209 | 1811.8651 | 1811.8651 | 2709.9189
11 | 0.9 | 0.86 | 20.5137 | 7.5 | 153.8527 |  | : | 233.9759 | 348.9835 | 574.7718 | 870.122 | 1221.163 | 1221.163 | 1826.4344 | 2224.8107 | 2568.743 | 2814.6268 | 2996.4061
15 | 0.9 | 0.9 | 26.73 | 7.5 | 200.4747 |  | : | : | 256.6983 | 423.4698 | 649.5479 | 937.1716 | 937.1716 | 1401.6822 | 1707.4129 | 1971.3609 | 2160.0625 | 2299.5675 | 2446.272 | 2597.9905
18.5 | 0.91 | 0.88 | 33.3457 | 7 | 233.4199 |  | : | : | : | 346.346 | 530.6703 | 795.3353 | 804.8982 | 1203.8472 | 1466.4267 | 1693.1208 | 1855.1888 | 1975.0039 | 2101.0024 | 2231.3071
22 | 0.91 | 0.85 | 41.0539 | 7 | 287.3773 |  | : | : | : | 290.2524 | 444.0284 | 653.7719 | 653.7719 | 977.8149 | 1191.0929 | 1375.2234 | 1506.8618 | 1604.1806 | 1706.5218 | 1812.3608 | 2750.4468
30 | 0.932 | 0.87 | 53.4045 | 7.3 | 389.8532 |  | : | : | : | : | 334.5946 | 481.923 | 481.923 | 720.7889 | 878.0052 | 1013.7356 | 1110.7718 | 1182.5097 | 1257.9498 | 1335.9682 | 2027.4712 | 2221.5437 | 2365.0194 | 2515.8995 | 2671.9363
37 | 0.936 | 0.87 | 65.5841 | 7.3 | 478.7641 |  | : | : | : | : | : | 392.4254 | 392.4254 | 586.9317 | 714.9515 | 825.4755 | 904.4912 | 962.9066 | 1024.3368 | 1087.8664 | 1650.9509 | 1808.9823 | 1925.8132 | 2048.6735 | 2175.7329 | 2476.4264 | 2713.4735
45 | 0.942 | 0.86 | 80.178 | 7.7 | 617.3707 |  | : | : | : | : | : | : | 304.3216 | 455.159 | 554.437 | 640.1471 | 701.4229 | 746.7234 | 794.3618 | 843.6284 | 1280.2941 | 1402.8458 | 1493.4468 | 1588.7236 | 1687.2567 | 1920.4412 | 2104.2686
55 | 0.946 | 0.86 | 97.581 | 7.7 | 751.3736 |  | : | : | : | : | : | : | 250.0477 | 373.9842 | 455.5565 | 525.9807 | 576.3284 | 613.5498 | 652.6922 | 693.1723 | 1051.9614 | 1152.6567 | 1227.0996 | 1305.3844 | 1386.3447 | 1577.9421 | 1728.9851
75 | 0.949 | 0.87 | 131.1197 | 7.4 | 970.2857 |  | : | : | : | : | : | : | : | : | 352.7756 | 407.311 | 446.2994 | 475.1231 | 505.4343 | 536.7815 | 814.622 | 892.5988 | 950.2462 | 1010.8686 | 1073.563 | 1221.933 | 1338.8982
90 | 0.952 | 0.87 | 156.8478 | 7.4 | 1160.6737 |  | : | : | : | : | : | : | : | : | : | 340.4988 | 373.0919 | 397.1876 | 422.5268 | 448.732 | 680.9977 | 746.1837 | 794.3751 | 845.0535 | 897.464 | 1021.4965 | 1119.2756
110 | 0.956 | 0.87 | 190.9008 | 7.7 | 1469.9359 |  | : | : | : | : | : | : | : | : | : | : | 294.5965 | 313.6226 | 333.6307 | 354.3225 | 537.7215 | 589.193 | 627.2453 | 667.2614 | 708.6451 | 806.5822 | 883.7894
132 | 0.958 | 0.87 | 228.6027 | 7.7 | 1760.2405 |  | : | : | : | : | : | : | : | : | : | : | : | 261.899 | 278.6072 | 295.8865 | 449.0387 | 492.0213 | 523.7979 | 557.2144 | 591.773 | 673.558 | 738.032
150 | 0.959 | 0.88 | 256.556 | 7.8 | 2001.1365 |  | : | : | : | : | : | : | : | : | : | : | : | : | 245.0686 | 260.2678 | 394.9836 | 432.792 | 460.7433 | 490.1372 | 520.5356 | 592.4754 | 649.188
185 | 0.96 | 0.88 | 316.0894 | 7.8 | 2465.4974 |  | : | : | : | : | : | : | : | : | : | : | : | : | : | 211.248 | 320.5909 | 351.2783 | 373.9652 | 397.8229 | 422.496 | 480.8864 | 526.9175
200 | 0.96 | 0.88 | 341.7183 | 7.6 | 2597.0589 |  | : | : | : | : | : | : | : | : | : | : | : | : | : | : | 304.3505 | 333.4833 | 355.0209 | 377.6701 | 401.0933 | 456.5257 | 500.225
[11 empty] | NOTES TO TABLE: | 1) | : = MOTOR FLA IS GREATER THAN CABLE AMPACITY
[12 empty] | 2) | NORMAL FONT = SIZE CONSTRAINED BY MOTOR RUNNING CONDITION
[12 empty] | 3) | ITALICS = SIZE CONSTRAINED BY MOTOR STARTING CONDITION
Starting
[34 empty] | Allowable cable volt drop % |  |  | 14.99%
[34 empty] | Allowable cable volt drop |  |  | 59.96 | V
[34 empty] | cos phi |  |  | 0.3
[34 empty] | sin phi |  |  | 0.95394
Running
[34 empty] | Allowable cable volt drop % |  |  | 4.99%
[34 empty] | Allowable cable volt drop |  |  | 19.96 | V
CABLE DATA
[34 empty] | Size |  | 2.5 |  |  | Size |  | 4 |  |  | Size |  | 6 |  |  | Size |  | 10 |  |  | Size |  | 16 |  |  | Size |  | 25 |  |  | Size |  | 35 |  |  | Size |  | 50 |  |  | Size |  | 70 |  |  | Size |  | 95 |  |  | Size |  | 120 |  |  | Size |  | 150 |  |  | Size |  | 185 |  |  | Size |  | 240 |  |  | Size |  | 2 x 95 |  |  | Size |  | 2 x 120 |  |  | Size |  | 2 x 150 |  |  | Size |  | 2 x 185 |  |  | Size |  | 2 x 240 |  |  | Size |  | 3 x 95 |  |  | Size |  | 3 x 120
[34 empty] | mV/A/m - R |  | 7.6386 |  |  | mV/A/m - R |  | 4.7786 |  |  | mV/A/m - R |  | 3.1886 |  |  | mV/A/m - R |  | 1.9186 |  |  | mV/A/m - R |  | 1.2386 |  |  | mV/A/m - R |  | 0.8126 |  |  | mV/A/m - R |  | 0.6076 |  |  | mV/A/m - R |  | 0.4696 |  |  | mV/A/m - R |  | 0.3486 |  |  | mV/A/m - R |  | 0.2736 |  |  | mV/A/m - R |  | 0.2326 |  |  | mV/A/m - R |  | 0.2046 |  |  | mV/A/m - R |  | 0.1786 |  |  | mV/A/m - R |  | 0.1548 |  |  | mV/A/m - R |  | 0.1368 |  |  | mV/A/m - R |  | 0.1163 |  |  | mV/A/m - R |  | 0.1023 |  |  | mV/A/m - R |  | 0.0893 |  |  | mV/A/m - R |  | 0.0774 |  |  | mV/A/m - R |  | 0.0912 |  |  | mV/A/m - R |  | 0.077533
[34 empty] | mV/A/m - X |  | 0.103 |  |  | mV/A/m - X |  | 0.096 |  |  | mV/A/m - X |  | 0.09 |  |  | mV/A/m - X |  | 0.084 |  |  | mV/A/m - X |  | 0.08 |  |  | mV/A/m - X |  | 0.079 |  |  | mV/A/m - X |  | 0.076 |  |  | mV/A/m - X |  | 0.076 |  |  | mV/A/m - X |  | 0.074 |  |  | mV/A/m - X |  | 0.073 |  |  | mV/A/m - X |  | 0.072 |  |  | mV/A/m - X |  | 0.072 |  |  | mV/A/m - X |  | 0.072 |  |  | mV/A/m - X |  | 0.072 |  |  | mV/A/m - X |  | 0.0365 |  |  | mV/A/m - X |  | 0.036 |  |  | mV/A/m - X |  | 0.036 |  |  | mV/A/m - X |  | 0.036 |  |  | mV/A/m - X |  | 0.036 |  |  | mV/A/m - X |  | 0.024333 |  |  | mV/A/m - X |  | 0.024
[29 empty] | PF (COS phi) | SIN (PHI) | FLA | LRC |  | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH | Volt Drop N | Volt Drop ST | L NOR | LST | LENGTH
[34 empty] | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m |  |  |  | mV/A/m | mV/A/m
[28 empty] | 0.55 | 0.67 | 0.74236 | 1.5799 | 8.3733 |  | 5.1943 | 2.3898 | 2432.2749 | 2996.3943 | 2432.2749 | 3.2729 | 1.5252 | 3860.1595 | 4695.1787 | 3860.1595 | 2.2032 | 1.0424 | 5734.4649 | 6869.3908 | 5734.4649 | 1.3478 | 0.65571 | 9373.6728 | 10920.804 | 9373.6728 | 0.88925 | 0.4479 | 14207.4941 | 15987.872 | 14207.4941 | 0.60309 | 0.31914 | 20948.876 | 22437.9998 | 20948.876 | 0.46351 | 0.25478 | 27257.2057 | 28106.239 | 27257.2057 | 0.37105 | 0.21338 | 34049.2592 | 33559.429 | 33559.429 | 0.2885 | 0.17517 | 43792.6182 | 40879.3102 | 40879.3102 | 0.2375 | 0.15172 | 53194.9256 | 47198.8216 | 47198.8216 | 0.20929 | 0.13846 | 60365.5506 | 51716.7614 | 51716.7614 | 0.19053 | 0.13006 | 66309.2122 | 55056.8252 | 55056.8252 | 0.17311 | 0.12226 | 72981.8085 | 58569.2619 | 58569.2619 | 0.15717 | 0.11512 | 80386.5139 | 62201.7443 | 62201.7443 | 0.11875 | 0.075859 | 106389.8512 | 94397.6432 | 94397.6432 | 0.10465 | 0.069232 | 120731.1012 | 103433.5228 | 103433.5228 | 0.095266 | 0.065032 | 132618.4245 | 110113.6504 | 110113.6504 | 0.086556 | 0.061132 | 145963.617 | 117138.5238 | 117138.5238 | 0.078583 | 0.057562 | 160773.0277 | 124403.4886 | 124403.4886 | 0.079168 | 0.050573 | 159584.7767 | 141596.4648 | 141596.4648 | 0.069764 | 0.046155 | 181096.6519 | 155150.2842 | 155150.2842
[28 empty] | 0.75 | 0.75 | 0.66144 | 1.9246 | 10.2002 |  | 5.7971 | 2.3898 | 1789.042 | 2459.7266 | 1789.042 | 3.6474 | 1.5252 | 2843.4171 | 3854.2512 | 2843.4171 | 2.451 | 1.0424 | 4231.4578 | 5639.0521 | 4231.4578 | 1.4945 | 0.65571 | 6939.5391 | 8964.8391 | 6939.5391 | 0.98187 | 0.4479 | 10562.7716 | 13124.3726 | 10562.7716 | 0.6617 | 0.31914 | 15673.5073 | 18419.2536 | 15673.5073 | 0.50597 | 0.31914 | 20497.719 | 18419.2536 | 18419.2536 | 0.40247 | 0.21338 | 25768.9634 | 27548.785 | 25768.9634 | 0.3104 | 0.17517 | 33412.8103 | 33557.6427 | 33412.8103 | 0.25348 | 0.15172 | 40914.5219 | 38745.3013 | 38745.3013 | 0.25348 | 0.13846 | 40914.5219 | 42454.0579 | 40914.5219 | 0.20107 | 0.13006 | 51579.2224 | 45195.9013 | 45195.9013 | 0.18157 | 0.12226 | 57118.5479 | 48079.2448 | 48079.2448 | 0.16372 | 0.11512 | 63345.9125 | 51061.1334 | 51061.1334 | 0.12674 | 0.075859 | 81829.0438 | 77490.6026 | 77490.6026 | 0.11104 | 0.069232 | 93403.4443 | 84908.1157 | 84908.1157 | 0.10054 | 0.065032 | 103158.4449 | 90391.8025 | 90391.8025 | 0.090787 | 0.061132 | 114237.0957 | 96158.4897 | 96158.4897 | 0.081862 | 0.057562 | 126691.825 | 102122.2667 | 102122.2667 | 0.084495 | 0.050573 | 122743.5656 | 116235.9039 | 116235.9039 | 0.074025 | 0.046155 | 140105.1665 | 127362.1736 | 127362.1736
[28 empty] | 1.1 | 0.73 | 0.68345 | 2.8247 | 14.1235 |  | 5.6466 | 2.3898 | 1251.4237 | 1776.4474 | 1251.4237 | 3.554 | 1.5252 | 1988.2603 | 2783.5916 | 1988.2603 | 2.3892 | 1.0424 | 2957.5967 | 4072.5986 | 2957.5967 | 1.458 | 0.65571 | 4846.5812 | 6474.5263 | 4846.5812 | 0.95885 | 0.4479 | 7369.4815 | 9478.5969 | 7369.4815 | 0.64719 | 0.31914 | 10918.3572 | 13302.6305 | 10918.3572 | 0.49549 | 0.31914 | 14261.1464 | 13302.6305 | 13302.6305 | 0.39475 | 0.21338 | 17900.5838 | 19896.0998 | 17900.5838 | 0.30505 | 0.17517 | 23164.0178 | 24235.777 | 23164.0178 | 0.24962 | 0.15172 | 28308.0896 | 27982.3732 | 27982.3732 | 0.24962 | 0.13846 | 28308.0896 | 30660.8866 | 28308.0896 | 0.19857 | 0.13006 | 35586.3957 | 32641.0825 | 32641.0825 | 0.17959 | 0.12226 | 39347.4297 | 34723.4717 | 34723.4717 | 0.16221 | 0.11512 | 43561.8 | 36877.0313 | 36877.0313 | 0.12481 | 0.075859 | 56616.1791 | 55964.7464 | 55964.7464 | 0.1095 | 0.069232 | 64530.1854 | 61321.7733 | 61321.7733 | 0.099283 | 0.065032 | 71172.7914 | 65282.165 | 65282.165 | 0.089793 | 0.061132 | 78694.8595 | 69446.9434 | 69446.9434 | 0.081106 | 0.057562 | 87123.6 | 73754.0627 | 73754.0627 | 0.083207 | 0.050573 | 84924.2687 | 83947.1196 | 83947.1196 | 0.073002 | 0.046155 | 96795.2781 | 91982.6599 | 91982.6599
[28 empty] | 1.5 | 0.76 | 0.64992 | 3.6061 | 19.8338 |  | 5.8723 | 2.3898 | 942.5648 | 1264.9932 | 942.5648 | 3.6941 | 1.5252 | 1498.3243 | 1982.1721 | 1498.3243 | 2.4818 | 1.0424 | 2230.2111 | 2900.0631 | 2230.2111 | 1.5127 | 0.65571 | 3658.9507 | 4610.4556 | 3658.9507 | 0.99333 | 0.4479 | 5572.17 | 6749.6288 | 5572.17 | 0.66892 | 0.31914 | 8274.5371 | 9472.691 | 8274.5371 | 0.51117 | 0.31914 | 10828.1024 | 9472.691 | 9472.691 | 0.40629 | 0.21338 | 13623.2756 | 14167.8448 | 13623.2756 | 0.31303 | 0.17517 | 17682.0027 | 17258.0923 | 17258.0923 | 0.25538 | 0.15172 | 21673.5626 | 19926.0118 | 19926.0118 | 0.25538 | 0.13846 | 21673.5626 | 21833.3586 | 21673.5626 | 0.20229 | 0.13006 | 27361.6596 | 23243.4394 | 23243.4394 | 0.18253 | 0.12226 | 30323.7208 | 24726.2912 | 24726.2912 | 0.16444 | 0.11512 | 33659.2064 | 26259.8228 | 26259.8228 | 0.12769 | 0.075859 | 43347.1252 | 39852.0237 | 39852.0237 | 0.11179 | 0.069232 | 49514.6158 | 43666.7173 | 43666.7173 | 0.10115 | 0.065032 | 54723.3192 | 46486.8788 | 46486.8788 | 0.091265 | 0.061132 | 60647.4416 | 49452.5823 | 49452.5823 | 0.082221 | 0.057562 | 67318.4128 | 52519.6456 | 52519.6456 | 0.085127 | 0.050573 | 65020.6878 | 59778.0355 | 59778.0355 | 0.074523 | 0.046155 | 74271.9237 | 65500.0759 | 65500.0759
[28 empty] | 2.2 | 0.78 | 0.62578 | 5.0261 | 29.1517 |  | 6.0226 | 2.3898 | 659.3925 | 860.6576 | 659.3925 | 3.7874 | 1.5252 | 1048.5428 | 1348.6013 | 1048.5428 | 2.5434 | 1.0424 | 1561.3702 | 1973.1026 | 1561.3702 | 1.5491 | 0.65571 | 2563.6182 | 3136.7944 | 2563.6182 | 1.0162 | 0.4479 | 3908.0385 | 4592.2139 | 3908.0385 | 0.68326 | 0.31914 | 5812.1451 | 6444.8911 | 5812.1451 | 0.52149 | 0.31914 | 7615.2062 | 6444.8911 | 6444.8911 | 0.41385 | 0.21338 | 9595.8907 | 9639.3112 | 9595.8907 | 0.31822 | 0.17517 | 12479.6894 | 11741.8087 | 11741.8087 | 0.25909 | 0.15172 | 15327.625 | 13556.9688 | 13556.9688 | 0.25909 | 0.13846 | 15327.625 | 14854.6615 | 14854.6615 | 0.20464 | 0.13006 | 19405.5553 | 15814.0317 | 15814.0317 | 0.18436 | 0.12226 | 21540.1608 | 16822.9127 | 16822.9127 | 0.1658 | 0.11512 | 23951.9294 | 17866.2746 | 17866.2746 | 0.12954 | 0.075859 | 30655.2499 | 27113.9376 | 27113.9376 | 0.11324 | 0.069232 | 35068.532 | 29709.3231 | 29709.3231 | 0.10232 | 0.065032 | 38811.1107 | 31628.0634 | 31628.0634 | 0.092182 | 0.061132 | 43080.3215 | 33645.8254 | 33645.8254 | 0.0829 | 0.057562 | 47903.8588 | 35732.5491 | 35732.5491 | 0.086363 | 0.050573 | 45982.8749 | 40670.9063 | 40670.9063 | 0.075495 | 0.046155 | 52602.798 | 44563.9846 | 44563.9846
[28 empty] | 3 | 0.75 | 0.66144 | 6.9562 | 45.2155 |  | 5.7971 | 2.3898 | 494.9683 | 554.8891 | 494.9683 | 3.6474 | 1.5252 | 786.6787 | 869.4795 | 786.6787 | 2.451 | 1.0424 | 1170.7033 | 1272.1123 | 1170.7033 | 1.4945 | 0.65571 | 1919.9392 | 2022.3758 | 1919.9392 | 0.98187 | 0.4479 | 2922.3668 | 2960.7238 | 2922.3668 | 0.6617 | 0.31914 | 4336.337 | 4155.1947 | 4155.1947 | 0.50597 | 0.31914 | 5671.0356 | 4155.1947 | 4155.1947 | 0.40247 | 0.21338 | 7129.4132 | 6214.7233 | 6214.7233 | 0.3104 | 0.17517 | 9244.2108 | 7570.26 | 7570.26 | 0.25348 | 0.15172 | 11319.6844 | 8740.5426 | 8740.5426 | 0.25348 | 0.13846 | 11319.6844 | 9577.2 | 9577.2 | 0.20107 | 0.13006 | 14270.2515 | 10195.7318 | 10195.7318 | 0.18157 | 0.12226 | 15802.7982 | 10846.1845 | 10846.1845 | 0.16372 | 0.11512 | 17525.7025 | 11518.868 | 11518.868 | 0.12674 | 0.075859 | 22639.3688 | 17481.0852 | 17481.0852 | 0.11104 | 0.069232 | 25841.6196 | 19154.4001 | 19154.4001 | 0.10054 | 0.065032 | 28540.5031 | 20391.4636 | 20391.4636 | 0.090787 | 0.061132 | 31605.5965 | 21692.369 | 21692.369 | 0.081862 | 0.057562 | 35051.4049 | 23037.736 | 23037.736 | 0.084495 | 0.050573 | 33959.0532 | 26221.6278 | 26221.6278 | 0.074025 | 0.046155 | 38762.4294 | 28731.6001 | 28731.6001
[28 empty] | 4 | 0.81 | 0.58643 | 8.4355 | 50.6129 |  | 6.2477 | 2.3898 | 378.7322 | 495.7149 | 378.7322 | 3.927 | 1.5252 | 602.5503 | 776.7569 | 602.5503 | 2.6355 | 1.0424 | 897.8003 | 1136.4523 | 897.8003 | 1.6033 | 0.65571 | 1475.8027 | 1806.7064 | 1475.8027 | 1.0502 | 0.4479 | 2253.13 | 2644.9876 | 2253.13 | 0.70453 | 0.31914 | 3358.5222 | 3712.0782 | 3358.5222 | 0.53672 | 0.31914 | 4408.5787 | 3712.0782 | 3712.0782 | 0.42494 | 0.21338 | 5568.2377 | 5551.9755 | 5551.9755 | 0.32576 | 0.17517 | 7263.5676 | 6762.9556 | 6762.9556 | 0.26443 | 0.15172 | 8948.4335 | 7808.4374 | 7808.4374 | 0.26443 | 0.13846 | 8948.4335 | 8555.8724 | 8555.8724 | 0.20795 | 0.13006 | 11378.7202 | 9108.443 | 9108.443 | 0.18689 | 0.12226 | 12660.9568 | 9689.5304 | 9689.5304 | 0.16761 | 0.11512 | 14117.1738 | 10290.4779 | 10290.4779 | 0.13221 | 0.075859 | 17896.8669 | 15616.8749 | 15616.8749 | 0.11531 | 0.069232 | 20519.4787 | 17111.7448 | 17111.7448 | 0.10397 | 0.065032 | 22757.4404 | 18216.8859 | 18216.8859 | 0.093444 | 0.061132 | 25321.9135 | 19379.0608 | 19379.0608 | 0.083805 | 0.057562 | 28234.3476 | 20580.9557 | 20580.9557 | 0.088142 | 0.050573 | 26845.3004 | 23425.3123 | 23425.3123 | 0.076876 | 0.046155 | 30779.2181 | 25667.6172 | 25667.6172
[28 empty] | 5.5 | 0.83 | 0.55776 | 11.1219 | 75.6288 |  | 6.3975 | 2.3898 | 280.5258 | 331.7465 | 280.5258 | 4.0198 | 1.5252 | 446.457 | 519.8279 | 446.457 | 2.6967 | 1.0424 | 665.4934 | 760.5463 | 665.4934 | 1.6393 | 0.65571 | 1094.779 | 1209.0995 | 1094.779 | 1.0727 | 0.4479 | 1673.0948 | 1770.1012 | 1673.0948 | 0.71852 | 0.31914 | 2497.7135 | 2484.2287 | 2484.2287 | 0.5467 | 0.31914 | 3282.727 | 2484.2287 | 2484.2287 | 0.43216 | 0.21338 | 4152.7874 | 3715.5405 | 3715.5405 | 0.33061 | 0.17517 | 5428.2896 | 4525.9629 | 4525.9629 | 0.2678 | 0.15172 | 6701.3767 | 5225.6292 | 5225.6292 | 0.2678 | 0.13846 | 6701.3767 | 5725.834 | 5725.834 | 0.20998 | 0.13006 | 8546.9393 | 6095.63 | 6095.63 | 0.1884 | 0.12226 | 9525.9516 | 6484.5103 | 6484.5103 | 0.16864 | 0.11512 | 10641.7743 | 6886.6815 | 6886.6815 | 0.1339 | 0.075859 | 13402.7534 | 10451.2584 | 10451.2584 | 0.11661 | 0.069232 | 15390.4787 | 11451.6681 | 11451.6681 | 0.10499 | 0.065032 | 17093.8785 | 12191.26 | 12191.26 | 0.094198 | 0.061132 | 19051.9032 | 12969.0206 | 12969.0206 | 0.084321 | 0.057562 | 21283.5486 | 13773.363 | 13773.363 | 0.089268 | 0.050573 | 20104.1301 | 15676.8876 | 15676.8876 | 0.077739 | 0.046155 | 23085.718 | 17177.5021 | 17177.5021
[28 empty] | 7.5 | 0.84 | 0.54259 | 14.8134 | 103.6938 |  | 6.4723 | 2.3898 | 208.1835 | 241.9584 | 208.1835 | 4.0661 | 1.5252 | 331.38 | 379.135 | 331.38 | 2.7273 | 1.0424 | 494.06 | 554.7023 | 494.06 | 1.6572 | 0.65571 | 813.0747 | 881.8533 | 813.0747 | 1.0838 | 0.4479 | 1243.209 | 1291.0183 | 1243.209 | 0.72545 | 0.31914 | 1857.3733 | 1811.8651 | 1811.8651 | 0.55162 | 0.31914 | 2442.6725 | 1811.8651 | 1811.8651 | 0.4357 | 0.21338 | 3092.556 | 2709.9189 | 2709.9189 | 0.33298 | 0.17517 | 4046.6305 | 3300.9982 | 3300.9982 | 0.26943 | 0.15172 | 5000.9811 | 3811.2978 | 3811.2978 | 0.26943 | 0.13846 | 5000.9811 | 4176.1208 | 4176.1208 | 0.21093 | 0.13006 | 6388.0291 | 4445.8304 | 4445.8304 | 0.18909 | 0.12226 | 7125.8491 | 4729.4592 | 4729.4592 | 0.1691 | 0.11512 | 7968.3179 | 5022.7816 | 5022.7816 | 0.13472 | 0.075859 | 10001.9622 | 7622.5956 | 7622.5956 | 0.11723 | 0.069232 | 11494.3665 | 8352.2415 | 8352.2415 | 0.10547 | 0.065032 | 12776.0582 | 8891.6608 | 8891.6608 | 0.094545 | 0.061132 | 14251.6982 | 9458.9183 | 9458.9183 | 0.084549 | 0.057562 | 15936.6358 | 10045.5631 | 10045.5631 | 0.089811 | 0.050573 | 15002.9434 | 11433.8934 | 11433.8934 | 0.07815 | 0.046155 | 17241.5498 | 12528.3623 | 12528.3623
[28 empty] | 11 | 0.86 | 0.51029 | 20.5137 | 153.8527 |  | 6.6218 | 2.3898 | 146.9412 | 163.0754 | 146.9412 | 4.1586 | 1.5252 | 233.9759 | 255.5298 | 233.9759 | 2.7881 | 1.0424 | 348.9835 | 373.8589 | 348.9835 | 1.6929 | 0.65571 | 574.7718 | 594.3525 | 574.7718 | 1.106 | 0.4479 | 879.7391 | 870.122 | 870.122 | 0.73915 | 0.31914 | 1316.39 | 1221.163 | 1221.163 | 0.56132 | 0.31914 | 1733.4346 | 1221.163 | 1221.163 | 0.44264 | 0.21338 | 2198.2023 | 1826.4344 | 1826.4344 | 0.33756 | 0.17517 | 2882.4952 | 2224.8107 | 2224.8107 | 0.27255 | 0.15172 | 3570.052 | 2568.743 | 2568.743 | 0.27255 | 0.13846 | 3570.052 | 2814.6268 | 2814.6268 | 0.2127 | 0.13006 | 4574.6195 | 2996.4061 | 2996.4061 | 0.19034 | 0.12226 | 5112.0263 | 3187.5665 | 3187.5665 | 0.16987 | 0.11512 | 5727.9883 | 3385.2603 | 3385.2603 | 0.13627 | 0.075859 | 7140.1041 | 5137.4861 | 5137.4861 | 0.11839 | 0.069232 | 8218.7706 | 5629.2537 | 5629.2537 | 0.10635 | 0.065032 | 9149.239 | 5992.8122 | 5992.8122 | 0.095169 | 0.061132 | 10224.0527 | 6375.133 | 6375.133 | 0.084935 | 0.057562 | 11455.9767 | 6770.5206 | 6770.5206 | 0.090849 | 0.050573 | 10710.1561 | 7706.2291 | 7706.2291 | 0.078926 | 0.046155 | 12328.156 | 8443.8805 | 8443.8805
[28 empty] | 15 | 0.9 | 0.43589 | 26.73 | 200.4747 |  | 6.9196 | 2.3898 | 107.9143 | 125.1509 | 107.9143 | 4.3426 | 1.5252 | 171.9546 | 196.1043 | 171.9546 | 2.909 | 1.0424 | 256.6983 | 286.915 | 256.6983 | 1.7634 | 0.65571 | 423.4698 | 456.131 | 423.4698 | 1.1496 | 0.4479 | 649.5479 | 667.7681 | 649.5479 | 0.76578 | 0.31914 | 975.1262 | 937.1716 | 937.1716 | 0.57997 | 0.31914 | 1287.5331 | 937.1716 | 937.1716 | 0.45577 | 0.21338 | 1638.3953 | 1401.6822 | 1401.6822 | 0.346 | 0.17517 | 2158.198 | 1707.4129 | 1707.4129 | 0.27806 | 0.15172 | 2685.4911 | 1971.3609 | 1971.3609 | 0.27806 | 0.13846 | 2685.4911 | 2160.0625 | 2160.0625 | 0.21552 | 0.13006 | 3464.706 | 2299.5675 | 2299.5675 | 0.19212 | 0.12226 | 3886.6944 | 2446.272 | 2446.272 | 0.1707 | 0.11512 | 4374.398 | 2597.9905 | 2597.9905 | 0.13903 | 0.075859 | 5370.9822 | 3942.7219 | 3942.7219 | 0.12036 | 0.069232 | 6204.0123 | 4320.1249 | 4320.1249 | 0.10776 | 0.065032 | 6929.412 | 4599.1349 | 4599.1349 | 0.096062 | 0.061132 | 7773.3888 | 4892.544 | 4892.544 | 0.085352 | 0.057562 | 8748.796 | 5195.9809 | 5195.9809 | 0.092687 | 0.050573 | 8056.4733 | 5914.0828 | 5914.0828 | 0.080241 | 0.046155 | 9306.0184 | 6480.1874 | 6480.1874
[28 empty] | 18.5 | 0.88 | 0.47497 | 33.3457 | 233.4199 |  | 6.7709 | 2.3898 | 88.4046 | 107.487 | 88.4046 | 4.2508 | 1.5252 | 140.8165 | 168.4259 | 140.8165 | 2.8487 | 1.0424 | 210.1221 | 246.4195 | 210.1221 | 1.7283 | 0.65571 | 346.346 | 391.7522 | 346.346 | 1.128 | 0.4479 | 530.6703 | 573.5185 | 530.6703 | 0.75261 | 0.31914 | 795.3353 | 804.8982 | 795.3353 | 0.57079 | 0.31914 | 1048.6908 | 804.8982 | 804.8982 | 0.44935 | 0.21338 | 1332.1093 | 1203.8472 | 1203.8472 | 0.34192 | 0.17517 | 1750.6578 | 1466.4267 | 1466.4267 | 0.27544 | 0.15172 | 2173.1617 | 1693.1208 | 1693.1208 | 0.27544 | 0.13846 | 2173.1617 | 1855.1888 | 1855.1888 | 0.21425 | 0.13006 | 2793.8804 | 1975.0039 | 1975.0039 | 0.19137 | 0.12226 | 3127.9207 | 2101.0024 | 2101.0024 | 0.17042 | 0.11512 | 3512.3261 | 2231.3071 | 2231.3071 | 0.13772 | 0.075859 | 4346.3234 | 3386.2416 | 3386.2416 | 0.11944 | 0.069232 | 5011.4091 | 3710.3776 | 3710.3776 | 0.10712 | 0.065032 | 5587.7609 | 3950.0078 | 3950.0078 | 0.095683 | 0.061132 | 6255.8414 | 4202.0047 | 4202.0047 | 0.085211 | 0.057562 | 7024.6521 | 4462.6143 | 4462.6143 | 0.091814 | 0.050573 | 6519.4851 | 5079.3624 | 5079.3624 | 0.079629 | 0.046155 | 7517.1137 | 5565.5663 | 5565.5663
[28 empty] | 22 | 0.85 | 0.52678 | 41.0539 | 287.3773 |  | 6.5471 | 2.3898 | 74.2607 | 87.3054 | 74.2607 | 4.1124 | 1.5252 | 118.2259 | 136.8026 | 118.2259 | 2.7577 | 1.0424 | 176.3014 | 200.1522 | 176.3014 | 1.6751 | 0.65571 | 290.2524 | 318.1975 | 290.2524 | 1.095 | 0.4479 | 444.0284 | 465.8357 | 444.0284 | 0.73233 | 0.31914 | 663.8985 | 653.7719 | 653.7719 | 0.5565 | 0.31914 | 873.6639 | 653.7719 | 653.7719 | 0.4392 | 0.21338 | 1107.0014 | 977.8149 | 977.8149 | 0.33529 | 0.17517 | 1450.05 | 1191.0929 | 1191.0929 | 0.27102 | 0.15172 | 1793.959 | 1375.2234 | 1375.2234 | 0.27102 | 0.13846 | 1793.959 | 1506.8618 | 1506.8618 | 0.21184 | 0.13006 | 2295.0992 | 1604.1806 | 1604.1806 | 0.18974 | 0.12226 | 2562.4236 | 1706.5218 | 1706.5218 | 0.16951 | 0.11512 | 2868.2364 | 1812.3608 | 1812.3608 | 0.13551 | 0.075859 | 3587.9179 | 2750.4468 | 2750.4468 | 0.11782 | 0.069232 | 4126.5781 | 3013.7235 | 3013.7235 | 0.10592 | 0.065032 | 4590.1984 | 3208.3612 | 3208.3612 | 0.094869 | 0.061132 | 5124.8472 | 3413.0436 | 3413.0436 | 0.084754 | 0.057562 | 5736.4729 | 3624.7215 | 3624.7215 | 0.090338 | 0.050573 | 5381.8769 | 4125.6701 | 4125.6701 | 0.078546 | 0.046155 | 6189.8672 | 4520.5853 | 4520.5853
[28 empty] | 30 | 0.87 | 0.49305 | 53.4045 | 389.8532 |  | 6.6964 | 2.3898 | 55.814 | 64.3565 | 55.814 | 4.2047 | 1.5252 | 88.8885 | 100.843 | 88.8885 | 2.8185 | 1.0424 | 132.6084 | 147.5407 | 132.6084 | 1.7106 | 0.65571 | 218.4914 | 234.5569 | 218.4914 | 1.117 | 0.4479 | 334.5946 | 343.3873 | 334.5946 | 0.74591 | 0.31914 | 501.065 | 481.923 | 481.923 | 0.56608 | 0.31914 | 660.2395 | 481.923 | 481.923 | 0.44602 | 0.21338 | 837.9617 | 720.7889 | 720.7889 | 0.33977 | 0.17517 | 1100.0187 | 878.0052 | 878.0052 | 0.27402 | 0.15172 | 1363.9313 | 1013.7356 | 1013.7356 | 0.27402 | 0.13846 | 1363.9313 | 1110.7718 | 1110.7718 | 0.2135 | 0.13006 | 1750.5759 | 1182.5097 | 1182.5097 | 0.19088 | 0.12226 | 1958.0239 | 1257.9498 | 1257.9498 | 0.17018 | 0.11512 | 2196.2649 | 1335.9682 | 1335.9682 | 0.13701 | 0.075859 | 2727.8626 | 2027.4712 | 2027.4712 | 0.11893 | 0.069232 | 3142.5903 | 2221.5437 | 2221.5437 | 0.10675 | 0.065032 | 3501.1518 | 2365.0194 | 2365.0194 | 0.095441 | 0.061132 | 3916.0477 | 2515.8995 | 2515.8995 | 0.085088 | 0.057562 | 4392.5298 | 2671.9363 | 2671.9363 | 0.091342 | 0.050573 | 4091.7939 | 3041.2068 | 3041.2068 | 0.079287 | 0.046155 | 4713.8854 | 3332.3155 | 3332.3155
[28 empty] | 37 | 0.87 | 0.49305 | 65.5841 | 478.7641 |  | 6.6964 | 2.3898 | 45.4488 | 52.4049 | 45.4488 | 4.2047 | 1.5252 | 72.3811 | 82.1155 | 72.3811 | 2.8185 | 1.0424 | 107.9818 | 120.141 | 107.9818 | 1.7106 | 0.65571 | 177.9155 | 190.9975 | 177.9155 | 1.117 | 0.4479 | 272.4573 | 279.6171 | 272.4573 | 0.74591 | 0.31914 | 408.0126 | 392.4254 | 392.4254 | 0.56608 | 0.31914 | 537.6269 | 392.4254 | 392.4254 | 0.44602 | 0.21338 | 682.3444 | 586.9317 | 586.9317 | 0.33977 | 0.17517 | 895.735 | 714.9515 | 714.9515 | 0.27402 | 0.15172 | 1110.6366 | 825.4755 | 825.4755 | 0.27402 | 0.13846 | 1110.6366 | 904.4912 | 904.4912 | 0.2135 | 0.13006 | 1425.4776 | 962.9066 | 962.9066 | 0.19088 | 0.12226 | 1594.4006 | 1024.3368 | 1024.3368 | 0.17018 | 0.11512 | 1788.398 | 1087.8664 | 1087.8664 | 0.13701 | 0.075859 | 2221.2731 | 1650.9509 | 1650.9509 | 0.11893 | 0.069232 | 2558.982 | 1808.9823 | 1808.9823 | 0.10675 | 0.065032 | 2850.9553 | 1925.8132 | 1925.8132 | 0.095441 | 0.061132 | 3188.8012 | 2048.6735 | 2048.6735 | 0.085088 | 0.057562 | 3576.7961 | 2175.7329 | 2175.7329 | 0.091342 | 0.050573 | 3331.9097 | 2476.4264 | 2476.4264 | 0.079287 | 0.046155 | 3838.473 | 2713.4735 | 2713.4735
[28 empty] | 45 | 0.86 | 0.51029 | 80.178 | 617.3707 |  | 6.6218 | 2.3898 | 37.5952 | 40.6394 | 37.5952 | 4.1586 | 1.5252 | 59.8632 | 63.6797 | 59.8632 | 2.7881 | 1.0424 | 89.2881 | 93.168 | 89.2881 | 1.6929 | 0.65571 | 147.0564 | 148.1164 | 147.0564 | 1.106 | 0.4479 | 225.0829 | 216.8399 | 216.8399 | 0.73915 | 0.31914 | 336.8008 | 304.3216 | 304.3216 | 0.56132 | 0.31914 | 443.5024 | 304.3216 | 304.3216 | 0.44264 | 0.21338 | 562.4141 | 455.159 | 455.159 | 0.33756 | 0.17517 | 737.4917 | 554.437 | 554.437 | 0.27255 | 0.15172 | 913.4044 | 640.1471 | 640.1471 | 0.27255 | 0.13846 | 913.4044 | 701.4229 | 701.4229 | 0.2127 | 0.13006 | 1170.4249 | 746.7234 | 746.7234 | 0.19034 | 0.12226 | 1307.9214 | 794.3618 | 794.3618 | 0.16987 | 0.11512 | 1465.5164 | 843.6284 | 843.6284 | 0.13627 | 0.075859 | 1826.8088 | 1280.2941 | 1280.2941 | 0.11839 | 0.069232 | 2102.7877 | 1402.8458 | 1402.8458 | 0.10635 | 0.065032 | 2340.8498 | 1493.4468 | 1493.4468 | 0.095169 | 0.061132 | 2615.8428 | 1588.7236 | 1588.7236 | 0.084935 | 0.057562 | 2931.0329 | 1687.2567 | 1687.2567 | 0.090849 | 0.050573 | 2740.2133 | 1920.4412 | 1920.4412 | 0.078926 | 0.046155 | 3154.1815 | 2104.2686 | 2104.2686
[28 empty] | 55 | 0.86 | 0.51029 | 97.581 | 751.3736 |  | 6.6218 | 2.3898 | 30.8903 | 33.3916 | 30.8903 | 4.1586 | 1.5252 | 49.1869 | 52.3228 | 49.1869 | 2.7881 | 1.0424 | 73.3641 | 76.5521 | 73.3641 | 1.6929 | 0.65571 | 120.8298 | 121.7008 | 120.8298 | 1.106 | 0.4479 | 184.9407 | 178.1678 | 178.1678 | 0.73915 | 0.31914 | 276.7344 | 250.0477 | 250.0477 | 0.56132 | 0.31914 | 364.4065 | 250.0477 | 250.0477 | 0.44264 | 0.21338 | 462.111 | 373.9842 | 373.9842 | 0.33756 | 0.17517 | 605.9646 | 455.5565 | 455.5565 | 0.27255 | 0.15172 | 750.5043 | 525.9807 | 525.9807 | 0.27255 | 0.13846 | 750.5043 | 576.3284 | 576.3284 | 0.2127 | 0.13006 | 961.6867 | 613.5498 | 613.5498 | 0.19034 | 0.12226 | 1074.6615 | 652.6922 | 652.6922 | 0.16987 | 0.11512 | 1204.1504 | 693.1723 | 693.1723 | 0.13627 | 0.075859 | 1501.0085 | 1051.9614 | 1051.9614 | 0.11839 | 0.069232 | 1727.7682 | 1152.6567 | 1152.6567 | 0.10635 | 0.065032 | 1923.3734 | 1227.0996 | 1227.0996 | 0.095169 | 0.061132 | 2149.3231 | 1305.3844 | 1305.3844 | 0.084935 | 0.057562 | 2408.3009 | 1386.3447 | 1386.3447 | 0.090849 | 0.050573 | 2251.5128 | 1577.9421 | 1577.9421 | 0.078926 | 0.046155 | 2591.6523 | 1728.9851 | 1728.9851
[28 empty] | 75 | 0.87 | 0.49305 | 131.1197 | 970.2857 |  | 6.6964 | 2.3898 | 22.7328 | 25.8579 | 22.7328 | 4.2047 | 1.5252 | 36.204 | 40.5179 | 36.204 | 2.8185 | 1.0424 | 54.0109 | 59.2807 | 54.0109 | 1.7106 | 0.65571 | 88.9907 | 94.2431 | 88.9907 | 1.117 | 0.4479 | 136.2791 | 137.9703 | 136.2791 | 0.74591 | 0.31914 | 204.0819 | 193.6329 | 193.6329 | 0.56608 | 0.31914 | 268.913 | 193.6329 | 193.6329 | 0.44602 | 0.21338 | 341.2986 | 289.6073 | 289.6073 | 0.33977 | 0.17517 | 448.0334 | 352.7756 | 352.7756 | 0.27402 | 0.15172 | 555.5239 | 407.311 | 407.311 | 0.27402 | 0.13846 | 555.5239 | 446.2994 | 446.2994 | 0.2135 | 0.13006 | 713.0028 | 475.1231 | 475.1231 | 0.19088 | 0.12226 | 797.4956 | 505.4343 | 505.4343 | 0.17018 | 0.11512 | 894.5302 | 536.7815 | 536.7815 | 0.13701 | 0.075859 | 1111.0479 | 814.622 | 814.622 | 0.11893 | 0.069232 | 1279.9649 | 892.5988 | 892.5988 | 0.10675 | 0.065032 | 1426.0056 | 950.2462 | 950.2462 | 0.095441 | 0.061132 | 1594.9911 | 1010.8686 | 1010.8686 | 0.085088 | 0.057562 | 1789.0604 | 1073.563 | 1073.563 | 0.091342 | 0.050573 | 1666.5718 | 1221.933 | 1221.933 | 0.079287 | 0.046155 | 1919.9473 | 1338.8982 | 1338.8982
[28 empty] | 90 | 0.87 | 0.49305 | 156.8478 | 1160.6737 |  | 6.6964 | 2.3898 | 19.0039 | 21.6164 | 19.0039 | 4.2047 | 1.5252 | 30.2653 | 33.8717 | 30.2653 | 2.8185 | 1.0424 | 45.1514 | 49.5567 | 45.1514 | 1.7106 | 0.65571 | 74.3933 | 78.7842 | 74.3933 | 1.117 | 0.4479 | 113.9249 | 115.3387 | 113.9249 | 0.74591 | 0.31914 | 170.6058 | 161.8708 | 161.8708 | 0.56608 | 0.31914 | 224.8026 | 161.8708 | 161.8708 | 0.44602 | 0.21338 | 285.3146 | 242.1024 | 242.1024 | 0.33977 | 0.17517 | 374.5414 | 294.909 | 294.909 | 0.27402 | 0.15172 | 464.4001 | 340.4988 | 340.4988 | 0.27402 | 0.13846 | 464.4001 | 373.0919 | 373.0919 | 0.2135 | 0.13006 | 596.0473 | 397.1876 | 397.1876 | 0.19088 | 0.12226 | 666.6805 | 422.5268 | 422.5268 | 0.17018 | 0.11512 | 747.7983 | 448.732 | 448.732 | 0.13701 | 0.075859 | 928.8001 | 680.9977 | 680.9977 | 0.11893 | 0.069232 | 1070.0093 | 746.1837 | 746.1837 | 0.10675 | 0.065032 | 1192.0946 | 794.3751 | 794.3751 | 0.095441 | 0.061132 | 1333.361 | 845.0535 | 845.0535 | 0.085088 | 0.057562 | 1495.5967 | 897.464 | 897.464 | 0.091342 | 0.050573 | 1393.2002 | 1021.4965 | 1021.4965 | 0.079287 | 0.046155 | 1605.0139 | 1119.2756 | 1119.2756
[28 empty] | 110 | 0.87 | 0.49305 | 190.9008 | 1469.9359 |  | 6.6964 | 2.3898 | 15.614 | 17.0685 | 15.614 | 4.2047 | 1.5252 | 24.8666 | 26.7454 | 24.8666 | 2.8185 | 1.0424 | 37.0972 | 39.1304 | 37.0972 | 1.7106 | 0.65571 | 61.123 | 62.2087 | 61.123 | 1.117 | 0.4479 | 93.603 | 91.0724 | 91.0724 | 0.74591 | 0.31914 | 140.1731 | 127.8146 | 127.8146 | 0.56608 | 0.31914 | 184.7022 | 127.8146 | 127.8146 | 0.44602 | 0.21338 | 234.42 | 191.1661 | 191.1661 | 0.33977 | 0.17517 | 307.7306 | 232.8626 | 232.8626 | 0.27402 | 0.15172 | 381.5602 | 268.8607 | 268.8607 | 0.27402 | 0.13846 | 381.5602 | 294.5965 | 294.5965 | 0.2135 | 0.13006 | 489.7241 | 313.6226 | 313.6226 | 0.19088 | 0.12226 | 547.7577 | 333.6307 | 333.6307 | 0.17018 | 0.11512 | 614.4057 | 354.3225 | 354.3225 | 0.13701 | 0.075859 | 763.1204 | 537.7215 | 537.7215 | 0.11893 | 0.069232 | 879.1405 | 589.193 | 589.193 | 0.10675 | 0.065032 | 979.4482 | 627.2453 | 627.2453 | 0.095441 | 0.061132 | 1095.5155 | 667.2614 | 667.2614 | 0.085088 | 0.057562 | 1228.8115 | 708.6451 | 708.6451 | 0.091342 | 0.050573 | 1144.6805 | 806.5822 | 806.5822 | 0.079287 | 0.046155 | 1318.7108 | 883.7894 | 883.7894
[28 empty] | 132 | 0.87 | 0.49305 | 228.6027 | 1760.2405 |  | 6.6964 | 2.3898 | 13.0389 | 14.2535 | 13.0389 | 4.2047 | 1.5252 | 20.7655 | 22.3344 | 20.7655 | 2.8185 | 1.0424 | 30.979 | 32.6769 | 30.979 | 1.7106 | 0.65571 | 51.0424 | 51.949 | 51.0424 | 1.117 | 0.4479 | 78.1656 | 76.0525 | 76.0525 | 0.74591 | 0.31914 | 117.0553 | 106.735 | 106.735 | 0.56608 | 0.31914 | 154.2405 | 106.735 | 106.735 | 0.44602 | 0.21338 | 195.7587 | 159.6383 | 159.6383 | 0.33977 | 0.17517 | 256.9786 | 194.4582 | 194.4582 | 0.27402 | 0.15172 | 318.632 | 224.5193 | 224.5193 | 0.27402 | 0.13846 | 318.632 | 246.0107 | 246.0107 | 0.2135 | 0.13006 | 408.9572 | 261.899 | 261.899 | 0.19088 | 0.12226 | 457.4197 | 278.6072 | 278.6072 | 0.17018 | 0.11512 | 513.0759 | 295.8865 | 295.8865 | 0.13701 | 0.075859 | 637.264 | 449.0387 | 449.0387 | 0.11893 | 0.069232 | 734.1498 | 492.0213 | 492.0213 | 0.10675 | 0.065032 | 817.9144 | 523.7979 | 523.7979 | 0.095441 | 0.061132 | 914.8395 | 557.2144 | 557.2144 | 0.085088 | 0.057562 | 1026.1519 | 591.773 | 591.773 | 0.091342 | 0.050573 | 955.8961 | 673.558 | 673.558 | 0.079287 | 0.046155 | 1101.2247 | 738.032 | 738.032
[28 empty] | 150 | 0.88 | 0.47497 | 256.556 | 2001.1365 |  | 6.7709 | 2.3898 | 11.4903 | 12.5377 | 11.4903 | 4.2508 | 1.5252 | 18.3025 | 19.6458 | 18.3025 | 2.8487 | 1.0424 | 27.3105 | 28.7433 | 27.3105 | 1.7283 | 0.65571 | 45.0161 | 45.6954 | 45.0161 | 1.128 | 0.4479 | 68.9735 | 66.8973 | 66.8973 | 0.75261 | 0.31914 | 103.3732 | 93.8863 | 93.8863 | 0.57079 | 0.31914 | 136.3029 | 93.8863 | 93.8863 | 0.44935 | 0.21338 | 173.1401 | 140.4211 | 140.4211 | 0.34192 | 0.17517 | 227.5406 | 171.0494 | 171.0494 | 0.27544 | 0.15172 | 282.4553 | 197.4918 | 197.4918 | 0.27544 | 0.13846 | 282.4553 | 216.396 | 216.396 | 0.21425 | 0.13006 | 363.1328 | 230.3717 | 230.3717 | 0.19137 | 0.12226 | 406.5495 | 245.0686 | 245.0686 | 0.17042 | 0.11512 | 456.5123 | 260.2678 | 260.2678 | 0.13772 | 0.075859 | 564.9106 | 394.9836 | 394.9836 | 0.11944 | 0.069232 | 651.3547 | 432.792 | 432.792 | 0.10712 | 0.065032 | 726.2656 | 460.7433 | 460.7433 | 0.095683 | 0.061132 | 813.099 | 490.1372 | 490.1372 | 0.085211 | 0.057562 | 913.0247 | 520.5356 | 520.5356 | 0.091814 | 0.050573 | 847.3659 | 592.4754 | 592.4754 | 0.079629 | 0.046155 | 977.032 | 649.188 | 649.188
[28 empty] | 185 | 0.88 | 0.47497 | 316.0894 | 2465.4974 |  | 6.7709 | 2.3898 | 9.3262 | 10.1763 | 9.3262 | 4.2508 | 1.5252 | 14.8554 | 15.9456 | 14.8554 | 2.8487 | 1.0424 | 22.1667 | 23.3297 | 22.1667 | 1.7283 | 0.65571 | 36.5376 | 37.089 | 36.5376 | 1.128 | 0.4479 | 55.9828 | 54.2976 | 54.2976 | 0.75261 | 0.31914 | 83.9035 | 76.2034 | 76.2034 | 0.57079 | 0.31914 | 110.6311 | 76.2034 | 76.2034 | 0.44935 | 0.21338 | 140.5302 | 113.9737 | 113.9737 | 0.34192 | 0.17517 | 184.6848 | 138.8333 | 138.8333 | 0.27544 | 0.15172 | 229.2566 | 160.2955 | 160.2955 | 0.27544 | 0.13846 | 229.2566 | 175.6392 | 175.6392 | 0.21425 | 0.13006 | 294.739 | 186.9826 | 186.9826 | 0.19137 | 0.12226 | 329.9784 | 198.9115 | 198.9115 | 0.17042 | 0.11512 | 370.5311 | 211.248 | 211.248 | 0.13772 | 0.075859 | 458.5132 | 320.5909 | 320.5909 | 0.11944 | 0.069232 | 528.6761 | 351.2783 | 351.2783 | 0.10712 | 0.065032 | 589.4781 | 373.9652 | 373.9652 | 0.095683 | 0.061132 | 659.9569 | 397.8229 | 397.8229 | 0.085211 | 0.057562 | 741.0622 | 422.496 | 422.496 | 0.091814 | 0.050573 | 687.7699 | 480.8864 | 480.8864 | 0.079629 | 0.046155 | 793.0142 | 526.9175 | 526.9175
[28 empty] | 200 | 0.88 | 0.47497 | 341.7183 | 2597.0589 |  | 6.7709 | 2.3898 | 8.6267 | 9.6608 | 8.6267 | 4.2508 | 1.5252 | 13.7412 | 15.1379 | 13.7412 | 2.8487 | 1.0424 | 20.5042 | 22.1478 | 20.5042 | 1.7283 | 0.65571 | 33.7973 | 35.2101 | 33.7973 | 1.128 | 0.4479 | 51.7841 | 51.547 | 51.547 | 0.75261 | 0.31914 | 77.6107 | 72.3431 | 72.3431 | 0.57079 | 0.31914 | 102.3338 | 72.3431 | 72.3431 | 0.44935 | 0.21338 | 129.9904 | 108.2 | 108.2 | 0.34192 | 0.17517 | 170.8334 | 131.8003 | 131.8003 | 0.27544 | 0.15172 | 212.0624 | 152.1752 | 152.1752 | 0.27544 | 0.13846 | 212.0624 | 166.7417 | 166.7417 | 0.21425 | 0.13006 | 272.6336 | 177.5105 | 177.5105 | 0.19137 | 0.12226 | 305.2301 | 188.835 | 188.835 | 0.17042 | 0.11512 | 342.7413 | 200.5466 | 200.5466 | 0.13772 | 0.075859 | 424.1247 | 304.3505 | 304.3505 | 0.11944 | 0.069232 | 489.0254 | 333.4833 | 333.4833 | 0.10712 | 0.065032 | 545.2672 | 355.0209 | 355.0209 | 0.095683 | 0.061132 | 610.4601 | 377.6701 | 377.6701 | 0.085211 | 0.057562 | 685.4825 | 401.0933 | 401.0933 | 0.091814 | 0.050573 | 636.1871 | 456.5257 | 456.5257 | 0.079629 | 0.046155 | 733.5381 | 500.225 | 500.225
[29 empty] | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 2x95 | 2X120 | 2X150 | 2X185 | 2X240 | 3x95 | 3x120
[28 empty] | 0.55 | Running | Running | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 0.75 | Running | Running | Running | Running | Running | Running | Starting | Running | Running | Starting | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 1.1 | Running | Running | Running | Running | Running | Running | Starting | Running | Running | Starting | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 1.5 | Running | Running | Running | Running | Running | Running | Starting | Running | Starting | Starting | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 2.2 | Running | Running | Running | Running | Running | Running | Starting | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 3 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 4 | Running | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 5.5 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 7.5 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 11 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 15 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 18.5 | Running | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 22 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 30 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 37 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 45 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 55 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 75 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 90 | Running | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 110 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 132 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 150 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 185 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting
[28 empty] | 200 | Running | Running | Running | Running | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting | Starting