## HV CABLES
UNDERGROUND (DIRECT BURIED) CABLE SELECTION CHART (ALUMINIUM - 33KV)
VOLTAGE |  | 33 | kV |  |  |  |  | CABLE RATING FACTORS:
CABLE DATA |  | OLEX HV CABLE (3C) | [8 empty] | SOIL TEMPERATURE RATING FACTOR | 1.18
CABLE MATERIAL |  | Aluminium | [8 empty] | SOIL THERMAL RESISTIVITY RATING FACTOR | 1.11
INSTALLATION METHOD |  | Direct Buried | [8 empty] | DEPTH OF BURIAL | 1
CONDUCTOR OPERATING TEMPERATURE |  | 90 | °C | [7 empty] | TOTAL DERATING FACTOR | 1.3098
AMBIENT AIR TEMPERATURE |  | 20 | °C | [7 empty] | ALLOWABLE CABLE VOLTAGE DROP | 5 | %
AMBIENT SOIL TEMPERATURE |  | 10 | °C | [7 empty] | POWER FACTOR | 0.9
SOIL THERMAL RESISTIVITY |  | 1.2 | K.m/W | [8 empty] | 100000
DEPTH OF BURIAL |  | 0.8 | m
Cable Size, mm² |  | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400 | 500
AC Resistance @ 50Hz - 90OC, ohms/km |  | 0 | 0 | 0 | 0.821 | 0.568 | 0.41 | 0.325 | 0.264 | 0.211 | 0.161 | 0.13 | 0.102 | 0.0815
Inductive Reactance @ 50Hz, ohms/km |  | 0 | 0 | 0 | 0.147 | 0.136 | 0.129 | 0.124 | 0.12 | 0.117 | 0.112 | 0.108 | 0.103 | 0.099
Impedance @ 50Hz, ohms/km |  | 0 | 0 | 0 | 0.83406 | 0.58405 | 0.42982 | 0.34785 | 0.28999 | 0.24127 | 0.19612 | 0.16901 | 0.14496 | 0.12823
Current Carrying Capacity (A) |  | 0 | 0 | 0 | 159 | 194 | 232 | 264 | 295 | 334 | 388 | 438 | 502 | 570
Derated Current Carrying Capacity (A) |  | 0 | 0 | 0 | 208.2582 | 254.1012 | 303.8736 | 345.7872 | 386.391 | 437.4732 | 508.2024 | 573.6924 | 657.5196 | 746.586
Maximum Cable Lengths (km)
LOAD | CURRENT (A) | MAXIMUM LENGTH (km) - 33KV
(KVA) | 33
40 | 0.69982 | : | : | : | 1695.2565 | 2386.1442 | 3201.2103 | 3928.0007 | 4695.4748 | 5650.7056 | 7026.9065 | 8296.4547 | 9958.1805 | 11684.2385
50 | 0.87477 | : | : | : | 1356.2052 | 1908.9154 | 2560.9682 | 3142.4005 | 3756.3798 | 4520.5645 | 5621.5252 | 6637.1637 | 7966.5444 | 9347.3908
75 | 1.3122 | : | : | : | 904.1368 | 1272.6102 | 1707.3122 | 2094.9337 | 2504.2532 | 3013.7097 | 3747.6835 | 4424.7758 | 5311.0296 | 6231.5939
100 | 1.7495 | : | : | : | 678.1026 | 954.4577 | 1280.4841 | 1571.2003 | 1878.1899 | 2260.2823 | 2810.7626 | 3318.5819 | 3983.2722 | 4673.6954
150 | 2.6243 | : | : | : | 452.0684 | 636.3051 | 853.6561 | 1047.4668 | 1252.1266 | 1506.8548 | 1873.8417 | 2212.3879 | 2655.5148 | 3115.7969
200 | 3.4991 | : | : | : | 339.0513 | 477.2288 | 640.2421 | 785.6001 | 939.095 | 1130.1411 | 1405.3813 | 1659.2909 | 1991.6361 | 2336.8477
250 | 4.3739 | : | : | : | 271.241 | 381.7831 | 512.1936 | 628.4801 | 751.276 | 904.1129 | 1124.305 | 1327.4327 | 1593.3089 | 1869.4782
500 | 8.7477 | : | : | : | 135.6205 | 190.8915 | 256.0968 | 314.2401 | 375.638 | 452.0565 | 562.1525 | 663.7164 | 796.6544 | 934.7391
750 | 13.1216 | : | : | : | 90.4137 | 127.261 | 170.7312 | 209.4934 | 250.4253 | 301.371 | 374.7683 | 442.4776 | 531.103 | 623.1594
1000 | 17.4955 | : | : | : | 67.8103 | 95.4458 | 128.0484 | 157.12 | 187.819 | 226.0282 | 281.0763 | 331.8582 | 398.3272 | 467.3695
1200 | 20.9946 | : | : | : | 56.5086 | 79.5381 | 106.707 | 130.9334 | 156.5158 | 188.3569 | 234.2302 | 276.5485 | 331.9393 | 389.4746
1500 | 26.2432 | : | : | : | 45.2068 | 63.6305 | 85.3656 | 104.7467 | 125.2127 | 150.6855 | 187.3842 | 221.2388 | 265.5515 | 311.5797
2000 | 34.9909 | : | : | : | 33.9051 | 47.7229 | 64.0242 | 78.56 | 93.9095 | 113.0141 | 140.5381 | 165.9291 | 199.1636 | 233.6848
2500 | 43.7387 | : | : | : | 27.1241 | 38.1783 | 51.2194 | 62.848 | 75.1276 | 90.4113 | 112.4305 | 132.7433 | 159.3309 | 186.9478
5000 | 87.4773 | : | : | : | 13.5621 | 19.0892 | 25.6097 | 31.424 | 37.5638 | 45.2056 | 56.2153 | 66.3716 | 79.6654 | 93.4739
6200 | 108.4719 | : | : | : | 10.9371 | 15.3945 | 20.653 | 25.3419 | 30.2934 | 36.4562 | 45.3349 | 53.5255 | 64.2463 | 75.3822
7500 | 131.216 | : | : | : | 9.0414 | 12.7261 | 17.0731 | 20.9493 | 25.0425 | 30.1371 | 37.4768 | 44.2478 | 53.1103 | 62.3159
10000 | 174.9546 | : | : | : | 6.781 | 9.5446 | 12.8048 | 15.712 | 18.7819 | 22.6028 | 28.1076 | 33.1858 | 39.8327 | 46.737
20000 | 349.9093 | : | : | : | : | : | : | : | 9.3909 | 11.3014 | 14.0538 | 16.5929 | 19.9164 | 23.3685
30000 | 524.8639 | : | : | : | : | : | : | : | : | : | : | 11.0619 | 13.2776 | 15.579
50000 | 874.7731 | : | : | : | : | : | : | : | : | : | : | : | : | :
Note: Shaded area indicates that load current is higher than cable current-carrying capacity.

## HV Current Rating (hidden)
| Copper |  | Aluminium |  | Copper |  | Aluminium
Nominal Conductor Area mm² | Direct Buried | Underground Wiring Enclosure | Direct Buried | Underground Wiring Enclosure | AC Resistance 50Hz, 90OC Ohms/km | Reactance 50Hz Ohms/km | AC Resistance 50Hz, 90OC Ohms/km | Reactance 50Hz Ohms/km
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
3.8/6.6kV Three Core Ind. Screened & PVC Sheathed
16 | 113 | 86 |  |  | 1.47 | 0.134
25 | 145 | 111 |  |  | 0.927 | 0.127
35 | 173 | 134 | 134 | 104 | 0.668 | 0.12 | 1.11 | 0.12
50 | 204 | 159 | 158 | 123 | 0.494 | 0.115 | 0.822 | 0.115
70 | 249 | 195 | 193 | 151 | 0.342 | 0.109 | 0.569 | 0.106
95 | 298 | 237 | 231 | 183 | 0.247 | 0.101 | 0.41 | 0.101
120 | 339 | 270 | 263 | 209 | 0.196 | 0.0969 | 0.325 | 0.0976
150 | 379 | 307 | 294 | 238 | 0.16 | 0.0942 | 0.265 | 0.0948
185 | 429 | 348 | 333 | 270 | 0.128 | 0.0917 | 0.211 | 0.0923
240 | 496 | 404 | 387 | 315 | 0.0986 | 0.089 | 0.162 | 0.0896
300 | 559 | 468 | 436 | 365 | 0.0798 | 0.0879 | 0.13 | 0.0885
400 | 634 | 532 | 500 | 420 | 0.064 | 0.0852 | 0.102 | 0.0857
500
6.35/11kV Three Core Ind. Screened & PVC Sheathed
16 | 113 | 89 |  |  | 1.47 | 0.142
25 | 145 | 114 |  |  | 0.927 | 0.134
35 | 173 | 136 | 134 | 106 | 0.668 | 0.127 | 1.11 | 0.127
50 | 204 | 162 | 158 | 126 | 0.494 | 0.121 | 0.821 | 0.121
70 | 249 | 199 | 193 | 154 | 0.342 | 0.115 | 0.569 | 0.112
95 | 299 | 242 | 231 | 188 | 0.247 | 0.106 | 0.41 | 0.106
120 | 340 | 276 | 263 | 214 | 0.196 | 0.102 | 0.325 | 0.103
150 | 380 | 310 | 295 | 240 | 0.16 | 0.099 | 0.265 | 0.0996
185 | 429 | 350 | 333 | 272 | 0.128 | 0.0961 | 0.211 | 0.0968
240 | 497 | 416 | 387 | 316 | 0.0985 | 0.0926 | 0.161 | 0.0933
300 | 560 | 470 | 437 | 366 | 0.0796 | 0.0904 | 0.13 | 0.091
400 | 635 | 534 | 500 | 420 | 0.0638 | 0.087 | 0.102 | 0.0876
500 | 710 | 597 | 567 | 477 | 0.0525 | 0.0847 | 0.0823 | 0.0847
12.7/22kV Three Core Ind. Screened & PVC Sheathed
16
25
35 | 173 | 140 | 134 | 109 | 0.668 | 0.141 | 1.11 | 0.14
50 | 204 | 168 | 158 | 130 | 0.494 | 0.134 | 0.821 | 0.134
70 | 250 | 205 | 194 | 159 | 0.342 | 0.127 | 0.568 | 0.124
95 | 299 | 246 | 232 | 191 | 0.247 | 0.117 | 0.41 | 0.117
120 | 340 | 280 | 264 | 217 | 0.196 | 0.112 | 0.325 | 0.113
150 | 381 | 321 | 295 | 249 | 0.16 | 0.109 | 0.265 | 0.11
185 | 430 | 363 | 334 | 281 | 0.128 | 0.105 | 0.211 | 0.106
240 | 498 | 421 | 388 | 327 | 0.0981 | 0.101 | 0.161 | 0.102
300 | 562 | 474 | 437 | 369 | 0.0792 | 0.0988 | 0.13 | 0.0996
400 | 638 | 539 | 501 | 423 | 0.0633 | 0.0944 | 0.102 | 0.0951
500 | 714 | 624 | 568 | 497 | 0.0518 | 0.0915 | 0.0819 | 0.0915
19/33kV Three Core Ind. Screened & PVC Sheathed Copper
16
25
35
50 | 205 | 170 | 159 | 132 | 0.494 | 0.147 | 0.821 | 0.147
70 | 250 | 213 | 194 | 165 | 0.342 | 0.139 | 0.568 | 0.136
95 | 299 | 255 | 232 | 197 | 0.247 | 0.128 | 0.41 | 0.129
120 | 341 | 290 | 264 | 224 | 0.196 | 0.123 | 0.325 | 0.124
150 | 381 | 324 | 295 | 251 | 0.159 | 0.12 | 0.264 | 0.12
185 | 431 | 366 | 334 | 284 | 0.128 | 0.116 | 0.211 | 0.117
240 | 499 | 424 | 388 | 330 | 0.0978 | 0.111 | 0.161 | 0.112
300 | 563 | 478 | 438 | 372 | 0.0788 | 0.107 | 0.13 | 0.108
400 | 640 | 562 | 502 | 440 | 0.0628 | 0.102 | 0.102 | 0.103
500 | 718 | 630 | 570 | 499 | 0.0513 | 0.099 | 0.0815 | 0.099

## Deratings (hidden)
Ambient Air Temperature Variation
Air temp. (°C) | Rating factor
20 | 1.18
25 | 1.14
35 | 1.05
40 | 1
45 | 0.95
50 | 0.89
55 | 0.84
Ground Temperature Variation
Ground temp. (°C) | Rating factor
10 | 1.11
15 | 1.07
20 | 1.04
25 | 1
30 | 0.96
35 | 0.92
40 | 0.88
Depth of Burial Variation
Depth, m | Direct Buried | Ducts
0.8 | 1 | 1
1 | 0.97 | 0.99
1.25 | 0.95 | 0.97
1.5 | 0.93 | 0.96
1.75 | 0.91 | 0.96
2 | 0.89 | 0.95
2.5 | 0.88 | 0.94
3 | 0.86 | 0.93